## Round 1
Input round 1 | RMI | BlueTack | IACS | Germany | France | Jensen Hughes | CSSF | Codan | Radicos | BIMCO | The Swedish Club | WSC
Q1. What can be done to improve the fire detection in a container cargo under deck? | There is still a lot to improve on the declaration side, additionally investigations should go report to the responsible enforcement organizations of the country where the cargo is assigned the carriage requirements. | A possible combination between smoke and heat detection. Containers with ‘fire hazardous’ cargo (if allowed under deck) could be ‘equipped’ with a remote sensor (not sure whether this technique is already available) | 1.1 Heat detectors and/or other linear detection systems can be fitted in cargo holds, e.g. fibre optics, thermal imaging cameras, video-based fire detection systems, laser beam detection capable of continuously monitoring and detecting both smoke as well as elevated levels of heat within the container holds. 1.2 Fire/Smoke/heat detectors can be fitted inside each container which give an alarm at the bridge; this option requires further maturity. 1.3 Enhanced smoke detection systems can also be considered: 1.3.1. Installation of aspirating smoke detection system (e.g. Very Early Stage Detection Apparatus) underneath of hatch covers 1.3.2. Increasing the number of smoke detectors on the FWD and AFT bulkheads, P&S longitudinal bulkheads of the cargo hold |  | Objectives: rapid detection and localization of a potential fire in the holds on board. Currently, 14mm copper pipes are installed, 100m long, which draw smoke in case of fire in the hold to the aft steering room. Proposals: Equip the holds with heat and smoke detectors with thermal cameras, preferably remotely adjustable. Use the cargo hold space ventilation which is extracting and sucks large volume in each hold. At the exit of each fan, make a bypass to divert some air and put a cell per hold at the exit of each fan. | Fire detection in cargo holds currently works on the same principles as when smoke aspiration systems were first designed around 1918. The principle issue is the lag time: a. Smoke production in container b. Smoke escaping from container c. Smoke being carried into extraction system, and d. Smoke travelling through pipe system to detection The spread of smoke and detection may also be affected by ambient temperatures and natural air flows in the hold. In the early stages of a fire the smoke is typically cooler and less buoyant, this and natural air flows may further delay transport of smoke to extraction system. The longer the delay in detection and alarm, the longer to deploy CO2, the less likely it is to be effective. • Any system must be capable of detecting trace amounts of smoke and gases from incipient fires and raise the alarm from within the hold of origin. • The detection system and the alarm system must be closer in proximity, reducing the lag time from detection to alarm • Consideration of network of distributed sensors • Thermal imaging cameras • CO detection – useful in smouldering fires • VESDA systems – series of smoke sampling pipes at high level, perhaps under hatch cover, designed for very early detection of smoke. Operation may also be influenced by some factors outlined above, maintenance and keeping sampling holes clean may be an issue. • Video detection | - Fitting of thermal detectors / temperature (CO2, humidity) sensors (possibly batteryless and wireless), sample smoke extraction with reduced response time, laser smoke detection with alarms in case of threshold temperature violation. (For example DNV Enhanced fire detection notation FCS(FD) requires enhanced smoke and heat detection systems installed in all cargo holds) - CFD (Computational Fluid Dynamics) testing may support the set-up of sensors/detectors. - Fitting CCTV systems (thermal/optical imaging) within the cargo area under deck to detect any abnormalities and continuous observation (possibly automated, AI). | A Cargo hold 1. Revisit the requirement for sensors – type and sensitivity. What is used in the onshore e.g. Sound spectrum analysis? 2. Location of sensors in cargo holds/ventilation – defined by fire simulations and not rigid rules. 3. Thermographic cameras and CCTV Container 4. Adhesive temperature gauge(s) (label) fitted on the container connected to an onboard network | Fires of containerized cargo are always "heating/temperature events". Hence, temperature is the first detectable physical parameter which deviates from regular condition and shows anomalies. Fires and incipient fires in containerized cargo can be detected and located in an early phase by a temperature monitoring system installed in the container cargo holds. Basic requirements for such systems are: a. One temperature measurement point (sensor) per container. b. Positioning of the temperature sensors in front (centered) of the container end wall with a max. distance of 20cm from the container wall. The blue dots in illustrations below indicate the sensor positions. c. Temperature measurement by all sensors at least every 5 seconds (data resolution). d. Analysis of spatial and temporal temperature gradients in real-time for alarming. Efficiency of this approach Such temperature monitoring systems allow: · Detection of container fires in an early phase when there is still ambient temperature around the concerned container in the cargo hold. · Exact localization (bay-row-tier coordinates) of the concerned container. The personnel on-board is informed about the exact location and in such an early phase that it is safe to approach the concerned container, to assess the situation and to take early and informed decisions on the further actions. Technological feasibility The requirements for continuous temperature monitoring of containers on a containership are very specific and rule out some technical approaches which work well in other application domains. The technological challenge is to measure/retrieve the temperature value of each container on a fullyladen containership. Optical systems Optical systems (thermal imaging, video-based systems) require unobstructed view to the objects to be monitored. On a containership an unobstructed view to containers is given only to a small percentage of the containers. Optical systems have the best reach on the vessel´s top area. There they could be used complementarily to other systems. Wireless solutions The space between containers on a laden containership is narrow and confined by metallic environment. These are adverse conditions for any approach based on wireless systems. Linear heat detection systems Linear heat detection systems (e.g. fibre-optical systems, sensor cables) are generally adequate for the fire detection application on containerships. Such systems are known from terrestrial applications. The actual suitability for fire detection of containerized cargo on containerships must be assessed individually for each linear heat detection system. Economic feasibility We can only speak for our own solution and expect the cost to be in the range of < 1% of the total cost of a container vessel. | Presently, given the placement of containers in the cargo hold and how the present smoke detection works, which is that the smoke travels through an extraction system and travels a long way to the detection sensor before triggering an alarm. Many a times, these detectors are located on the bridge of a ship, which means the smoke has to travel a very long distance before it gets analysed and alarms the crew member. With the increase in the size of the ship this problem gets worse. While the smoke is travelling, the fire is getting intense and spreading at the same time. Not only this, but the cargo ventilator fans in the cargo also holds, which are running most of the time is aerating the fire, by supplying fresh oxygen in order for the combustion to carry on and intensify. These fans also dissipate the smoke from reaching the smoke extraction lines, therefore, more time is wasted before the alarms are activated. There have been cases where the fire was first spotted by a member of the crew, rather than the fire detection system. Therefore, we need to find ways to reduce the time between the actual start of the fire to the time it is detected positively by the ship’s crew members. The first few moments of a fire are crucial and the present set up does not help to act fast. | • Installation of fixed thermal (infrared) imaging system covering at least the gables of all containers stowed below deck. Output connected to intelligent signal processing for automatic detection and alarm. • Installation of (several) remote IoT CO2 sensors (ref https://www.manxtechgroup.com/forest-fire-detection-using-iot-and-co2-sensors/) at strategic locations in the cargo hold. An increase of CO2 content will trigger an alarm and prompt further investigation. • Installation of remote thermal sensing system, one measuring point for each container (ref https://www.radicos.com/), with intelligent signal processing/alarm. • Installation of video analytics software on (existing) CCTV circuit for long range detection of smoke/mist. (ref https://www.fike.com/products/fike-video-analytics/) | Carrier One 1. Improving crew familiarization with limitations of CH Smoke Detection units to ensure operational readiness, maintenance schedules carried out and followed up. 2. Testing of the Fire Detection Equipment to be done in a timely manner to verify efficiency of the equipment 3. Installation of temperature sensors can be considered inside the cargo holds at key locations (including bottom & mid-level) initiating an alarm if temperature is noted beyond present levels. 4. Increasing the number of sampling lines for smoke detection system (branching at each tier level inside cargo hold). 5. Dedicated smoke sampling and fire alarm system (for set of 2 to 3 cargo holds) – reducing length of smoke sampling sensing lines. 6. Installation of cameras capable of sensing change of picture or smoke due to density. 7. Installation of infrared smoke sensors arrangement inside cargo hold. 8. Improve planning system and do NOT allow self-heating substances under deck 9. install heat sensors with remote alert capability in containers with self-heating (the remote alert capability can be part of a fire extinguishing system in those specific containers). Carrier Two Enhanced cargo hold monitoring notation could be considered, alarms in case of threshold temperature violation is possible. For example DNV Enhanced fire detection notation FCS(FD) requires enhanced smoke and heat detection systems installed in all cargo holds. Carrier Three Thermal imaging cameras/flame detector sensors, can aid to detection at all levels in the hold, enabled with visual and audible alarm (Example: https://www.flir.asia/instruments/early-fire-detection/ )
Q2. What can be done to improve the fire detection in a container cargo on deck? | It is difficult to improve under the current circumstances but we might have to think of individual fire/smoke detection systems per container which can be linked with the cargo stowage plan and fire detection system. | Use of thermal imaging cameras could be an option (Stena Line has them installed on the top deck of their ferries) | 2.1 Heat or linear/beam smoke detectors can be fitted on deck. 2.2 Fire/Smoke/heat detectors can be fitted inside each container which give an alarm at the bridge; this option requires further maturity. 2.3 Continuous surveillance by TIC (Thermal Imaging Camera) with image analysis which are installed on ship’s top area (ship’s bridge above (compass deck), and funnel casing top in case of 2 islands type container vessel). TIC should be operated by optimized programming like a zig-zag pattern for full coverage (as per cargo loading condition). (ex.) |  | Currently there is no detection. Detection is only visual. Use thermal cameras in each bay that measure the temperature of each container front. We could set an alarm at 50°c for example. Keynote: install thermal cameras or thermal sensor with alarm thresholds in the bays. Disadvantages: high cost. Install thermal cameras inside protective boxes. Important spare. | • Must be capable of detecting trace amounts of smoke and gases from incipient fires • Network of distributed sensors/zones/addressable system • Heat tracing • Thermal imaging cameras • CO Detection – useful for smouldering fires • Video smoke detection | - Fitting of thermal detectors / temperature sensors (possibly batteryless and wireless) for continuous measuring of surface temperature, laser smoke detection - Fitting CCTV systems (thermal/optical imaging) within the cargo area on deck to detect any abnormalities and continuous observation (possibly automated, AI). (For example FCS(FD) requires installation of camera-based on-deck heat (fire) detection system) | - Thermographic cameras and CCTV Container - Adhesive temperature gauge(s) (label) fitted on the container connected to an onboard network | See input given above on question 1 "What can be done to improve the fire detection in a container cargo under deck?" Specifics for solutions on deck: The temperature sensors must be positioned close to the containers. Hence, temperature sensor systems need to be mounted on the ship structure. Under deck there is no limitation – all containers may be reached, e.g. by using the cell guide structure. On deck containers might be stacked higher than the cell guide structure. Hence, these containers cannot be covered by such sensor systems. An optical system (thermal imaging cameras) could be used as a complementary solution to monitor the temperature of the containers on the highest tier level. See illustrated example below: Green: Containers which can be monitored by linear heat detection systems fixed on cell guides. Yellow: Containers which could be monitored additionally by thermal imaging cameras. Red: Non-reachable containers | Detecting a fire on deck can be equally difficult if not more, depending on the placement of the burning container. If a burning container is located in front of the accommodation and possibly on the top tier, the crew, especially the bridge officers will most probably, not miss it. If the same container is located on the sides near the walkways, the crew working on deck will detect sooner or later. But if the same container is located in the middle of a stow, hidden behind the accommodation block or in a place where the movement of crew is minimum, it is quite difficult to detect the burning container before it reaches a stage where it produces visible flame, smoke that can be seen or smelt or smoke that produces strong enough odour for the crew members to detect it. Until then, a burning container on deck, in most cases are not detected. We need to look into this in detail to ensure that any burning container on deck is known to the ship’s staff at the earliest possible time. | • Considering the outdoor environment we believe thermal (infrared) imaging system connected to intelligent signal processing is the most robust solution. As a general comment, in a perfect world there is 100% fire detection coverage on each and every box onboard the vessel. Possibly this can be achieved for newbuilding’s at some point in time. A quick fix is to attach self-powered and wi-fi enabled remote sensor on selected boxes with dangerous cargo and otherwise suspected content. This is not a bullet proof solution as faulty declared containers will slip through the net but it might improve the situation somewhat. Relatively quick deployment and manageable cost. | Carrier One 10. Installation of camera for cross deck views. 11. install heat sensors with remote alert capability in containers with self-heating (the remote alert capability can be part of a fire extinguishing system in those specific containers). Carrier Two For example FCS(FD) requires installation of camera-based on-deck heat (fire) detection system. Typical enhanced detection systems incl.: Sample smoke extraction with reduced response time Laser smoke detection Thermal imaging Optical imaging Carrier Three Thermal/flame/smoke detecting cameras on deck
Q3. What can be done to enable a more precise and quick fire localisation? | See answer on question 2 | Use of thermal imaging cameras in combination with Remote sensors | 3.1 Reduce the detection time of sample smoke detection systems, or augment with other fire detection systems. 3.2 Cutting the air supply is the most efficient way for under deck fire. 3.3 Increase number of detectors/locate them considering the natural/forces air movement 3.4 For holds fitted with forced ventilation, initiate ventilation shutdown upon detection of fire, this could be automatic when fire is confirmed. 3.5 For holds using natural ventilation, initiate closure of the ventilation openings upon detection of fire 3.6 To keep fire in a localized area (in the cargo hold) install underdeck sprinklers 3.7 In case of on-deck fire, it is a big challenge to isolate burning container(s) from others. In addition, open atmosphere condition makes firefighting more difficult (cannot isolating from air supply). A foam application system can be helpful to cut air supply, so installation (adoption of new system especially for on-deck fire) of deck foam firefighting system can be considered. It would be an engineering challenge due to the need for sea water & foam supply, boost pumps, foam tanks and spaces in the lashing bridges, etc.. 3.8 Suitable fire detectors installed INSIDE the containers, these detectors are addressable, which will be linked to stowage position on board. When there is a fire inside a container, alarm (as well as the position signal) will be given out at very early stage of ignition. This option requires further development. |  | See answers to the 2 previous questions. Each container could have its own fire detection with a “wifi” connection. To see if technically this solution works properly subject to electromagnetic compatibility. If possible, investigate the feasibility of such an installation. It is interesting to think about the design of the container as a whole (reinforcement of joints/seals, detection with “wifi” connection, waterproofing of the container sides...) Provid the ship a portable thermal imaging camera. | a. Network of distributed sensors b. Zones c. Addressable detection d. Thermal imaging e. Linking of detection to ventilation systems for automatic operation, closing/stopping when fire detected. System could be linked to voice messaging alerting crew to fire and location | - Fitting of thermal detectors / temperature sensors (batteryless), laser smoke detection. E.g. scanning entire deck with thermal sensors permanently installed in high-up positions such as funnel, bridgewing, wheelhouse top. (For example a notation or solution similar to Enhanced fire detection with container identification FSC (FD+)) - Fitting CCTV systems (thermal/optical imaging) within the cargo area (on and under deck) to detect any abnormalities and continuous observation (possibly automated, AI). However fixed installations are prone to damage during discharge and loading of cargo, therefore mobile equipment solutions would seem to be a good possibility - Minimum number of handheld thermal scanners/cameras as a part of the standard firefighting equipment. - Risk evaluation based: Equip containers with high risk cargo on the outside e.g. with dataloggers, install systems on board that gather this data and trigger alarms in case of fire. | Interconnect A 2,3,4 and container data (age, type of container with cargo manifest) in a machine learning monitoring model supported by ship and shore. | Localization In general, the achievable degree of localization of a sensor system depends on the measurement resolution of the sensor system. Hence, if a fire/heating event in containerized cargo should be localized, the concerned container needs to be identified. Consequently, an adequate fire detection system must provide (at least) one sensor per container. Quick and precise fire detection For the precise and quick detection of a fire/heating event of containerized cargo the temperature gradients must be identified very early and need to be correctly interpreted. This can be achieved by: · Adequate data resolution and real-time analysis. Measurement by all sensors at least every 5 seconds. The analysis needs to be conducted continuously in real-time ("live-analysis"). · Energy flow analysis If the temperate of one container rises (temporal gradient) it must be compared to the temperatures of the adjacent containers (spatial gradients): - If an adjacent temperature is higher, then there is no fire/heating event in the observed container. In that case the energy flows in from the outside and might be caused e.g. by the sun, heated fuel, other heat sources or a fire in an adjacent container. - If the temperature of the observed container is higher than the temperatures of the adjacent containers, there is definitely a fire/heating event in the observed container and an alarm shall be triggered. · False alarm avoidance Analysis of spatial temperature gradients is required to prevent false alarms which would be triggered if only temporal temperature gradients (temperature rise of a container) are taken into account. · Additional temperature sensors Under deck additional temperature sensors should be provided to measure the temperature of the hull next to each container or at least at each tier level in a bay (starboard and port). In this manner spatial temperature gradient analysis can also be conducted for those containers adjacent to the hull and increases the efficiency of the fire detection system. | At present, the best possible localisation for a fire underdeck is to know which cargo hold is on fire. Some of the ships carry up to 120 containers in a single cargo hold. To pin-point where in the cargo hold a container is on fire, we need better detection system. The system needs to be better in two ways – to reduce the time of detection and locate where exactly in the cargo hold, (in terms of length, breadth, and height of the cargo hold) the fire is burning in a more accurate manner. The existing detection systems are clearly not enough to reach this level of localisation. | • With modern detection systems such as IoT, CCTV and/or infrared camera sensor the location will be automatically and precisely located. | Carrier One 12. Use “Smart Containers” with t° alerts / smoke detectors / NXT / TRX 13. Other actions for improving the reliability of the detection system could be addressed to the reduction of the air exchange between the CH and the open deck by means of: • non weather tight type hatch cover on container vessels can be provided with inflatable packing between pontoons to air seal cargo hold when required; • Installation of plates with limited openings between hatches in same cargo hold; • Installation of plates with limited openings between Port, Stbd, Centre part of cargo hold; • Ramnek tapes can be supplied to all vessels in quantity adequate to cover the largest single CH onboard. Carrier Two For example a notation or solution similar to Enhanced fire detection with container identification FSC (FD+) On deck: Thermal sensors based on risk goal-based evaluation scanning entire deck space. For example thermal sensors permanently installed in high-up positions such as funnel, bridgewing, wheelhouse top. Under deck: Thermal sensors could assist in early detection, however fixed installations are prone to damage during discharge and loading of cargo wherefore mobile equipment solutions would seem a good possibility. Carrier Three -- Sufficient water monitor capability for each bay on deck to fully cover all the stacks of that bay. -- Fixed water sprinkler system in the cargo hold. -- Alarm systems with thermal detections to point out exact location on the effected bay (e.g. heat detected at 53-02-12 ETC)
Q4. What can be done to compensate the deficiencies of CO2 with regard to smothering a fire in a container stow under deck? | Additionally to the water mist lances the installment of an Internationally Universe Connections on a container where a fire extinguish system can be connected on, the C02 deficiencies would be limited as mostly would be contained in the container. | Not much from the outset 1) It is almost impossible that CO2 will actually penetrate into a single container. 2) CO2 is used to fill the cargo space but that only has a limited effect. Due to the movement of the ship, the many openings and the effects of wind (etc.) it will be impossible to maintain the minimal level of CO2 needed to ‘control’ the fire spread in that specific hold. | 4.1 Main engine’s exhaust gases can be utilized as an inert gas for the purpose of supplementary use only. This could be an easy option for ship owners in the aspect of budget and its efficiency. Minimizing air leaks through the non-weathertight hatch covers would be essential. 4.2 Provide an option for cargo hold flooding, as a last resort; this requires stability and structural aspects to be considered as well as ensuring pumping arrangements to drain the cargo hold to prevent developing a list. 4.3 Suitable self-contained fire fighting equipment is to be arranged inside containers or fire fighting piping (including nozzles and other fitting) connected from the ship’s relating fire fighting systems is to be led inside containers. This option requires further development. |  | Foam would be effective, but depending on the load, if for example the hold is nearly empty, this would mean too much foam and a large volume of foam to store. In this case, container slots would have to be removed. A fire-fighting system with water spray already exists in holds with dangerous cargo. These are small diameter hoses and to extinguish a fire the hold would have to be drowned and therefore larger diameter hoses would have to be used to send the water from above or from the bottom of the hold. But if we drown the hold, we modify the structure of the ship (important constraints). The solution of foam or gas extinguishing does not seem possible and not very effective in both cases. Actions to remember are: Cooling, isolating the problematic container, containing the fire and smothering the fire if possible. Therefore, the basic requirement is to equip the holds with a powerful hi-fog water system with a cooling agent and the water cannon deck with a cooling agent. This system must be vertical (fixed to the ceiling) and horizontal (fixed to the walls of each hold). It should be noted that a comparison is interesting between a container ship that has containers in the hold and on deck and a ropax ship that has cargo in its garages and on deck. | The assumption is that CO2 is ineffective, largely due to the very serious casualties that occur such as, Flaminia, Honam etc. There are many casualties where CO2 is successful and we hear little about why, influencing factors could be: • Speed of detection • Speed of alarm • Speed of muster • Speed of deployment fire teams • Speed that vents are closed • Location of fire • Speed of C02 release • Adherence to CO2 release instructions and frequency of top ups • Crew training • Competence of crew • Command training • Competence of Command team • Adequacy and detail of emergency response plans Understanding why some responses are successful and some are not, may inform future plans. From a firefighting perspective CO2 is an effective extinguishing medium, could be augmented from exhaust gas ventilation In 1994 Class NK undertook some tests regarding the control of fire in engine rooms using CO2. The test results indicated that the faster the release of CO2 into the space, the greater the chance of success. Whilst I am not aware of any similar studies looking at hold fires, it seems reasonable to assume this same principle will apply. Therefore any changes must be geared towards faster detection and response | - Automated operation (closing) of mechanical and natural ventilation - A risk evaluation based approach such as the Risk-Zone Based Dangerous Goods Stowage Concept where only Dangerous Goods that can effectively be extinguished with existing Fixed Fire Fighting CO2 solutions, is stowed under deck. - There are many cargoes that will flare up again once CO2 begins to dissipate where for only cargoes that can effectively be extinguished permanently should be placed under deck, similarly all oxidizing cargoes should be placed on deck only. - But also: In addition to CO2 as a fire-fighting medium, sprinkler system could be fitted inside cargo holds (as hatch covers on container vessels are not airtight, efficiency of CO2 as an extinguishing agent remains questionable). - General considerations to hatch coaming effectiveness could be relevant as well as inspection program. | - Quick response – release. - CO2 system decentralized and capacity increased - System modification of ME exhaust system – connect exhaust system to cargo hold bilge system and inert the cargo hold with a booster fan. Unlimited exhaust gas. |  | Co2 has been both successful and unsuccessful in fighting fires. The fires where Co2 has been unsuccessful, has created some devastating effects. Co2 fights the fire by cutting off the oxygen of the fire. But if the fire happens because of a chemical reaction which produces its own oxygen, Co2 extinguishment is quickly put out of the equation. Secondly, whenever Co2 is used, it should cut off the oxygen supply by creating an air-tight barrier until the fire is completely extinguished and the cargo temperature reduces enough to ensure there is no reignition. Currently, the cargo holds of a containership do not have such airtight sealing. Therefore, these shortcomings have to be compensated. | • For a CO2 system to function properly the space subject to extinguishing need to be enclosed. An inflatable and fire proof curtain/pillow installed in a recess in the hatch coaming will work as a seal to ensure that the CO2 is confined inside the cargo hold. Deployed simultaneously as the CO2 is released. | Carrier One 14. Water drenching nozzles on underside of hatch covers can be provided as an additional measure. 15. Provision of high expansion foam concentrates with fixed nozzles/concentrate containers provisions at tank top level inside cargo hold with drive water and valves located outside cargo hold 16. Use “smart fire fighting system” / “smart containers” Carrier Two A risk evaluation-based approach such as the Risk-Zone Based Dangerous Goods Stowage Concept where only Dangerous Goods that can effectively be extinguished with existing Fixed Fire Fighting CO2 solutions, are stowed under deck. There are many cargoes that will flare up again once CO2 begins to dissipate where for only cargoes that can effectively be extinguished permanently should be placed under deck, similarly all oxidizing cargoes should be placed on deck only. General considerations to hatch foaming effectiveness could be relevant as well as inspection program. Carrier Three High expansion foam in cargo hold has already been developed and can address this issue (Example : https://kashiwa-tech.co.jp/en/fire-ex/fire-ex-d8/ )
Q5. What can be done to improve the confinement of a fire in containers under deck to the particular cargo hold? | See the first part of answer on question 4, additional the communication should be ensured for the crewmembers to provide boundary cooling and other tasks unhindered and for that two-way portable communication equipment with sufficient reception inside the cargo holds and on deck. | Once a container is on fire, it is of importance that the container on fire is detected and localized as quickly as possible. This enhances the response of the crew and therefore the chance to control the fire and to avoid fire spread. | 5.1 Hatch cover mounted water spray systems could be a viable option, for container ships fitted with hatch covers. 5.2 Provide a water spray system on bulkheads and water spray curtains between container bays. 5.3 Additional structural fire insulation requirements for bulkheads between cargo holds could offer protection for shorter periods of time. 5.4 Other PFP (passive fire protection) for all boundaries (fwd, aft, port, starboard, underside of hatch/deck, tank top) similar to that used for offshore facilities. NB this could be expensive and what would be sufficient will require further research. (see also 8.4) 5.5 Consideration of whether the fire is within a cargo hold having boundaries with heated fuel tanks (or even above LNG fuel tanks) is also important. 5.6 Increase survey attendance to verify integrity of bulkheads 5.7 Suitable self-contained fire fighting equipment is to be arranged inside containers or fire fighting piping (including nozzles and other fitting) connected from the ship’s relating fire fighting systems is be led inside containers. These equipment/arrangement can extinguish a fire at very early stage of ignition and limit the fire and damage within the container of the origin. This option requires further development. |  | See question 4. There are too many variable parameters that come into play (limited access, containers close to each other). No means to my knowledge. | • Early detection and response are key to minimising fire size. • The use of water spray/drenching to provide water curtains and protect water tight or intermediate bulkheads . Associated risk of capsize to be considered and ability of bilge system to manage excess water and dispose/recycle • Structural insulation enhanced. • Very early detection of fire could provide opportunity for fire teams to enter hold. Availability of firefighting equipment in hold would reduce arduous nature of hold, confined space entry, with fire hose. However, there is no certainty that box of origin will be accessible, and that crew are not being exposed to greater risk with limited escape route and potentially unknown cargo. | - Enhanced detection - Mandatory fire protection and fireproof insulation of electric wires. - Sprinkler/flooding systems - A notation or solution similar to DNV Fire-fighting notation FCS(FF) could be considered. The notation requires a permanently installed cooling system to be installed in all cargo holds. The cooling system shall consist of water spray nozzles, fixed supply piping system and remotely operated stop valves. Further defined requirement that the cooling system shall be able to distribute water uniformly on the upper surfaces of all top (under deck) containers and underside surfaces and open supporting structure of the hatch covers. | - Response time - Passive fire protection insulation – AX0 maintain |  | This can be achieved by 1. Detection of the fire by the quickest possible means. 2. Cutting the ventilation to create an air-tight compartment. This can be achieved easily for under-deck cargo but presently the cargo hatch cover design does not allow an air-tight sealing. 3. Activation of the firefighting system (fixed or portable). 4. Cutting off one or more of the fire triangle (heat, oxygen, fuel). 5. Boundary cooling of the area to prevent hotspots and to stop the spread of fire by radiation. | • See pt. 4 above. • Suggest to install piping for a deluge system covering sections of the stacks in the cargo hold thus enabling partial deluge of a few stack only at a time. To keep down installation cost, and maintain the possibility for retrofit, piping can be open-ended on deck with manual connections directly to fire hose(s). Bilge pumping system to be dimensioned accordingly to avoid flooding of CH when the system is in use. | Carrier One 17. Have void spaces between cargo holds or fixed sprinkler nozzle rail arrangement on forward and aft bulkhead for continuous boundary cooling for cargo hold having container on fire. 18. Fitting of fire insulation (A-60 Class) on bulkheads separating CHs could be considered, where feasible. 19. The concept of fire containment can be part of the ship’s planning, by, for example: • avoiding the stowage “en mass” of container carrying certain material (e.g. ammonium nitrate) ; • combination planning when possible to create extra fire protection walls by selecting your cargoes; • select cargoes that require the same fire fighting approach-attack; • Avoid heated tanks/spaces Carrier Two A notation or solution similar to DNV Fire-fighting notation FCS(FF) could be considered. The notation requires a permanently installed cooling system to be installed in all cargo holds. The cooling system shall consist of water spray nozzles, fixed supply piping system and remotely operated stop valves. Further defined requirement that the cooling system shall be able to distribute water uniformly on the upper surfaces of all top (under deck) containers and underside surfaces and open supporting structure of the hatch covers. The Risk-Zone Based Dangerous Goods Stowage Concept does not allow stowage of Dangerous goods adjacent to accommodation and engine room under deck structure i.e. stowage of Dangerous Goods is only possible where removed by a fire proof bulkhead, thus restricting development of under deck fire to cargo space between fire proof bulkheads away from critical areas essential to crew safety and vessel maneuverability. Carrier Three -- High expansion foam flooding as mentioned above. -- Fixed sprinkler system -- Water flooding of one cargo hold (prevention of progressive flooding, dewatering system, structural strength, special class notation ETC required)
Q6. What can be done to improve the confinement of a fire in containers on deck to the particular bay or section thereof? | See the answer on question 5. | See answer point 5. This in combination with, for example: 1) water monitors, 2) a ‘mobile and easy to deploy deluge system, 3) a fixed sprinkler/deluge system in between particular bay or sections (in combination with a certain degree of segregation of fire hazardous cargo). | 6.1 Water spray systems that create spray ‘curtains’ between container bays. 6.2 Provide water deluge systems with suitable structural and stability aspects accounted for. 6.3 Attaching portable temperature monitoring sensors on the FWD and AFT wall (for easy installation and maintenance) and checking temperature rise during the voyage. They can be grouped and systemized for early stage fire detection in the container boxes. Measuring devices transmitting temperature information to the receiver periodically then the internal temperature of container laid under supervision. The receiving device activates an alarm to the officer in charge when the temperature rise is acknowledged. 6.4 Suitable self-contained fire fighting equipment is to be arranged inside containers or fire fighting piping (including nozzles and other fitting) connected from the ship’s fire fighting systems is to be led inside containers. The equipment/arrangements can extinguish a fire at very early stage of ignition and limit the fire and damage within the container of the origin. This option requires further development. |  | See question n°4. Install fixed guns directed between each crossway located on the port, starboard and center (if possible) to make a water curtain. See the "FiFi" guns installed on AHTS and PSV vessels in the Oil&Gas field. The tests are done with fresh water and in case of fire, switch to the seawater circuit. Keynote: Install fixed guns at the lashing bridges, which can be started simply from the bridge like a fire pump. | • Early detection and response (2/3 above) • Use of water sprays, drenchers at intermediate positions could provide water curtains from, typically tier 3, down. Upper tiers would require water monitors at frequent intervals to keep fire size to minimum area. • Remote operated water monitors | - Enhanced detection - Mandatory fitting of remote controlled fixed/semi portable type water monitors / hypermist systems in crossbays / on lashing bridges on new ships (portable water monitors have their own limitations related to carrying heavy fire-fighting equipment to the site of fire). - Firefighting equipment to reach and fight fires inside containers in the top tiers (e.g. Hydro Pen) - The Risk-Zone Based Dangerous Goods Stowage Concept does not allow Dangerous Goods to be stowed next to accommodation or engine room, minimum 40’ separation is required. The 40’ gives crew an improved distancing when on-deck firefighting and improves successful fire extinguishing before breaching accommodation and engine room access | - Response time - Water Monitors fitted on every lashing bridge for remote operation |  | For fires on deck, the available ways to suppress the fire is to cut off either the fuel or heat as cutting of the oxygen supply is difficult unless the container is still intact, and a firefighting medium exists within the container. Cutting off fuel – When a cargo in a container is burning, it is again difficult to cut off the fuel in that container however, it is still possible to cut off the cargo in the other containers from the fire so they do not start burning as well. Cutting off Heat – This is probably the most effective way of dealing with a fire on deck unless the fire is of a nature where water cannot be used such as live electric fire, oil fire etc. | • A fixed long distance deluge system (aka MSC) on bridge/funnel wings enabling deluge of any stack on deck. • Alternatively, for existing ships and to keep installation cost down, a portable booster pump/deluge unit connected to the normal fire system with capacity to provide sufficient throw length for deluge of any stack on deck. High-rise type fire nozzle(s) with fixed mount capability to be connected to the unit. | Carrier One 20. Provision for fixed water sprinkler lines/nozzles adjoining lashing bridge area facing containers. 21. Provision for fixed nozzles for water lance on all cross decks. 22. Refer to the planning stage as per 19. Carrier Two Similar to the considerations of under deck stowage of Dangerous Goods, the Risk-Zone Based Dangerous Goods Stowage Concept does not allow Dangerous Goods to be stowed next to accommodation or engine room, minimum 40’ separation is required. The 40’ gives crew an improved distancing when on-deck firefighting and improves successful fire extinguishing before breaching accommodation and engine room access. Additionally, fire-fighting equipment such as fixed or portable water monitors can provide extra water curtains between bay areas or from bridge wings enabling colling and shielding from bay at fire. Carrier Three Make water curtains by using strategically placed remote controlled water monitors to adequately separate effected bay from adjacent bays
Q7. What can be done to improve active firefighting on deck bearing in mind reduced crew and local conditions? | See answer on question 4, with the addition of the crew providing boundary cooling with the possibility to use hoses and nozzles that can be fixed at effective places with pre-installed equipment that can hold and aim the nozzles. | See point 6 | 7.1 Additional requirements for water monitors, which could be remotely controlled, mounted on top of the accommodation (or engine casing for large twin island container ships). 7.2 Make SOLAS reg. II-2/10.7.3.1 applicable to vessels carrying less than five tiers of containers. 7.3 Suitable self-contained fire fighting equipment is to be arranged inside containers or fire fighting piping (including nozzles and other fitting) connected from the ship’s relating fire fighting systems is to be led inside containers. This option requires further development. 7.4 Several accidents have taken place in the night or the early hours of morning. Fire Drills during night time may help crew and company identify more effective options. 7.5 Remote mechanism for automatically closing the forced and natural ventilation flaps for cargo holds. 7.6 Another aspect is the small distance between the containers. It is very difficult for crew to approach site of fire considering heat, toxic gases, reduced visibility while being donned with firefighters suits and BA. There is always possibility of container exploding depending upon the nature of cargo which may be a threat to crew. Also keep the human element in mind. These are not trained firefighters. 7.7 Equipment needs to be reviewed with regards to replenishment of the BA sets. The location and accessibility to such sets should also be improved. 7.8 Access to shore support and technical experts may also help in helping Master with strategy for firefighting. 7.9 Improved means of access (physical access as well as visual access considering smoke and light conditions) to the cargo holds and container stacks to control fire at the fire source containers, considering crew equipped with firefighters suits and BA sets. Better equipment and fittings require to quickly penetrate a container and cool it. Consideration that access routes to the concerned holds may be blocked due to fallen containers or exploded containers or debris. 7.10 Providing sufficient number of hoses (with adequate lengths) which are compatible with the hydrants. |  | See previous answers. We can also imagine a gantry / overhead crane equipped with guns that would have its station at sea at the level of the bridge/castle and that could move on rails along the length of the ship but that would require losing a row of containers in width. Another solution is to post fixed but steerable guns at different strategic locations (such as the bridge) with enough power to be within reach of all the container bays. Keynote: Install steerable guns at the monkey bridge and the front mast, which can be started simply from the bridge like a fire pump. | • Remote operated water monitors-current portable provision too heavy and cumbersome • Increased no. of fire lockers along length of ship to improve accessibility and reduce travel times to scene of operations • Improved fire training day/night • Consideration needs to be given to adequacy of equipment provision, ppe, duration of Breathing apparatus sets, spare cylinders, replenishment of air • Increase provision of hose and modernise firefighting branches/nozzles, combined straight stream and spray • Provision of thermal imaging cameras for firefighting teams • Consider no. and positioning of fire hydrants • Consider fire hydrants on lashing bridges – riser systems fed by hose or fixed pipework | - Early detection - Mandatory fitting of remote controlled fixed/semi portable type water monitors / hypermist systems in crossbays / on lashing bridges on new ships (portable water monitors have their own limitations related to carrying heavy fire-fighting equipment to the site of fire). - Higher/additional pump capacity/pressure for effective cooling - The Risk-Zone Based Dangerous Goods Stowage Concept provides distancing to the fire and increases possibility of firefighting with adequate distance and without exposure to direct heat radiation. - Firefighting equipment to reach and fight fires inside containers in the top tiers (e.g. Hydro Pen) - Additional SCBAs and compressors - Additional (enhanced) Fireman’s outfits - Additional hoses - (Mandatory) more realistic training scenarios | - Remote operation of fire hydrants supported by intel from sensor systems (analysis) and shore experts - Crew should monitor the fire from distance – report and revise remote operation of systems. |  | We have seen in the Maersk Honam case that the presence of the extra portable fire fighting equipment did not help the crew members much. The ships are getting bigger, and the number of containers is increasing. As of now, there is no requirement of a permanent fire-fighting system for on deck cargo except fire hydrants and hoses, but these cannot be operated without the presence of crew on site. Without looking into more fixed firefighting systems that can be operated remotely, increasing the number of portable fire fighting equipment may not solve the problem in all cases of on deck firefighting systems. | • See pt. 6. • Mandatory “HydroPen” or similar technology allowing penetration and deluge of any container anywhere. Mandatory crew training at regular intervals (ref https://hydropenfire.com/) | Carrier One 23. Same as per question no. 6. 24. Use arrangements similar to HydroPen. 25. Use water monitors capable of delivering water through the deck’s length. Carrier Two Ad 6 as well. The Risk-Zone Based Dangerous Goods Stowage Concept provides distancing to the fire and increases possibility of firefighting with adequate distance and without exposure to direct hear radiation. Additional Fire-fighting equipment such as fixed or portable water monitors can provide extra water curtains between bay areas and once installed does not need permanent manning. Carrier Three -- Remote controlled water monitors fixed at appropriate heights as mentioned above -- Remote controlled ventilation closing arrangements for cargo holds (must be fire resistant system) -- A plan that provides quick firefighting guideline for each bay -- Dedicated cargo fire control station -- Registering with shore based quick action support team specialized in container cargo fire
Q8. What can be done to protect vital ship structures under deck and on deck from excessive heat? | See answer on question 4, with the installment of an water spray system to protect the structure. | 1) distance, 2) ‘fire proofing 3) the use of water as cooling medium | 8.1 Additional structural fire insulation requirements for ship structures under deck would be effective protection for short periods of time. Flooding the holds may help in controlling the temperatures but there are strength and stability issues which need to be considered. For containers on deck, boundary cooling may be helpful. Though it should be kept in mind that some nearby containers may contain cargo which may be reactive to water. This should be taken into account. 8.2 Provide fire protection coatings on key structure 8.3 Suitable water spray system is to be provided. 8.4 Application of Passive Fire Protection (see also 5.4) could be a solution. There is some limit to apply A-60 insulation for hold and on-deck. For example, Insulation affected on the cargo hold inside are easily damaged by water/cargo/weather and maintaining original condition is not easy also. But PFP is strong against mechanical damages and moisture. And maintenance is not required unless it affected by deep impact damages such as falling objects. |  | See question n°4. It would be necessary to create a void space between the cargo hold 1st in front of the castle and the engine hold. Install horizontal and vertical hi-fog water mist protection in each cargo hold. | • Drencher systems to protect external exposures • Increased structural fire protection accommodation block/navigation bridge • Blast protection – accomodation block/navigation bridge – create place of safety • Placement of remote monitors on top of accomodation block | - Water curtains / sprinkler systems (additional firefighting equipment on such as fixed or portable water monitors on deck can provide extra water curtains between bay areas and once installed does not need permanent manning). - The Risk-Zone Based Dangerous Goods Stowage Concept is designed to protect hull integrity, vessel stability and vessel manoeuvrability. It should be considered to imbed the Risk-Zone Based Dangerous Goods Stowage Concept in SOLAS and the IMDG Code as mandatory DG Stowage. - As the engine room is vital for the safe running and continuity of firefighting on board, it must be protected from a fire in the adjoining cargo holds by fireproof insulated bulkheads (heat from the engine room should also not be allowed to spread to the adjoining cargo holds, which could contain cargo sensitive to heat). - Cofferdams around LNG fuel tanks | - Vital structures are defined as the engine room on Maersk Honam? - Revisit IMDG code – could a barrier of specific low risk cargoes or empty container be stowed adjacent. |  | To look into adding more heat resistant material. To look into ways of cooling down these structures from the beginning of the fire so the rise of temperature is better controlled. | n/a | Carrier One 26. Have guards with fixed sprinkler nozzle rail arrangement on forward and aft bulkhead inside cargo holds and on lashing bridge for continuous boundary cooling & ensuring containment within the area affected. 27. It should not be disregarded the need of pumping out of water. Carrier Two The Risk-Zone Based Dangerous Goods Stowage Concept is designed to protect hull integrity, vessel stability and vessel maneuverability. It should be considered to imbed the Risk-Zone Based Dangerous Goods Stowage Concept in SOLAS and the IMDG Code as mandatory DG Stowage. On deck: Additional Fire-fighting equipment such as fixed or portable water monitors can provide extra water curtains between bay areas and once installed does not need permanent manning. Underdeck: Water spray for cooling Carrier Three Heat resistant paint/steel (A-60 class ETC)
Q9. What can be done to improve the protection of deck house and life-saving appliances? | The installment of a water spray system protecting the “critical” equipment. | The best way is to adopt part of the fire safety measures, concerning sprinklers/deluges/water monitors, applicable on tankers. | 9.1 Protection of LSA. 9.1.1 Adding structure to shield the lifeboats and liferafts adjacent to the accommodation. 9.1.2 Adding water spray systems covering that area (e.g. similar to requirements of IGC Code reg. 11.3). 9.1.3 An MES can be required in order to increase the possibility to evacuate the vessel. 9.2 Deckhouse protection: 9.2.1 Adoption of tanker-like structural fire insulation requirements for the accommodation (e.g. SOLAS reg. II-2/9.2.4.2.5) would be effective for short periods of time. PFP methods can also be used (see also 5.4) 9.2.2 Provide enhanced structural fire protection (including windows) 9.2.3 Provide water spray system 9.2.4 Provide auto closure of ventilation openings 9.2.4 Provide a water monitor to cover on-deck area close to the accommodation block can be fitted. |  | See question n°4. Install water curtains like on tankers and fire protection A60 & camera. It is also necessary to guarantee the continuity of navigation and manoeuvres at sea in the case of a fire on the deck at the front of the castle, so consider cameras with screens available to the officer on watch in the wheelhouse. | • Water spray/mist to protect fire lockers/Lifeboats • Drencher systems • Protection of windows • Positive pressure in accomodation and passageways to prevent ingress of smoke • Automate ventilation closure • Ensure hazardous cargo not stowed adjacent to accomodation block/near engine room | - No DG cargo near living quarters / engine room / LSA: The Risk-Zone Based Dangerous Goods Stowage Concept does not allow stowage of Dangerous goods adjacent to accommodation and engine room under deck structure i.e. stowage of Dangerous Goods is only possible where removed by a fire proof bulkhead, thus restricting development of under deck fire to cargo space between fire proof bulkheads away from critical areas essential to crew safety and vessel maneuverability. - Detailed evaluation of life saving appliances positioning could be relevant based on the latest major fire incidents - Fitting of mist/spray systems around the accommodation and LSA equipment | Fixed water spray, closed ventilations system as on tankers |  | There are a number of existing systems on other types of ships such as water curtains, water spray systems etc. Location of Life saving appliances and improvement on these to better resist a fire incident can be looked into. | n/a | Carrier One 28. Provision of fixed sea water cooling of accommodation block plating forward and aft during fire on containers (a similar provision is provided in the IGC Code). LSA must be similarly protected or ensured located not in extreme close vicinity to the bays Fwd and Aft. They must be located within safe distance of not less than 2 m from the fwd and aft bays. 29. Specific substances not to be loaded in the vicinity of the safe zone – this is mainly made via DOC for DG, but can be optimized. 30. Consider improvement of PPE (e.g. firemen outfits). Carrier Two Ad 8. As well. Detailed evaluation of life saving appliances positioning could be relevant based on the latest major fire incidents in conjunction with possible water spray system protection deck house and/or life-saving appliances. Carrier Three -- Heat resistant paint/steel(A-60 class)/ portholes. -- positive pressure air ventilation system (with air intakes strategically positioned and powered by emergency source too) . -- Dedicated assembly station for crew (not fighting afire ) to shelter during a firefighting adequately sheltered from deck fire with easy access to life boats -- Water spray system for accommodation exteriors and lifeboat stations In addition, a focused training schedule of the crew on cargo fire can be emphasized.
General comments |  |  | GC1: The objective of the firefighting has to be clarified for containerships. It may not be possible to extinguish the fire by the crew themselves. Rather they could keep it under control until external assistance arrives. GC2: Also the misdeclaration, improper stowage of cargo within containers, mis-stowage of containers, deficient containers (e.g. DG containers with clogged ventilation openings) etc. are the fundamental problems industry has to address. Improving traceability using blockchain might be an option. GC3: There are of course complexities with the technical nature of the cargo which are beyond the Crew’s training, e.g. MSC Flaminia accident, cargo may be appropriate to transport on land but marine transportation would require some additional considerations which are not taken into account when shipping. Industry has to ponder over the need to limit number and quantity of dangerous goods or cargo carried onboard. | The scope of work, in order to contribute to this output, is focusing risks and identifying risk control options. In order to focus the risks, a screening of the output of the risk analysis (ref. MSC 102/INF.3) should be made, so that the effort is focused on the areas most needing risk control. Referring to MSC 102/INF.3 in principle, the severity of cargo-related fires can be reduced by improvement of the two following key points 1. measures to improve an early detection and localisation of the fire, and 2. measures to prevent the fire from spreading to adjacent sections (fire compartments). Furthermore it is important to bear in mind that the formulation of the technical solutions should not be prescriptive but follow the GBS approach. | Do a risk analysis beforehand to know the source of the fires on these ships, such as misdeclaration of the contents of the containers. | No single solution, must consider: • Regulatory framework – are regulations adequate/can IMO keep pace with change requirements • Design of ships – increasing ship size increases time to respond allowing fire growth which makes successful outcome more difficult. Should SOLAS require companies and builders to consider ship design impact on ability to fight fire? An example could be, increased size imposes longer response times, company and builders must look to introduce compensating measures. Class/competent 3rd party must consider if measures are adequate. • Fire protection o Passive o Active • Crew training/competency • Safe carriage of cargo Emerging risks • Green fuels o Hydrogen o Ammonia o Electricity o Other • All introduce new risks/hazards that ship, and crew will need to be equipped to deal with. Implications for emergency response training/firefighting equipment/techniques/ Whilst there may be many possible solutions, it is likely that testing will have to be undertaken to assess suitability for this environment. | Generally, it should be noted that classification societies are working on notation that seek to address the raised topics, some are referred to here but should not be seen as an exhaustive investigation. Reference is made to the Risk-Zone Based Dangerous Goods Stowage Concept which is published under the name: Safety Considerations for Ship Operators Related to Risk‐Based Stowage of Dangerous Goods on Containerships. We find it imperative to mention that we are of the firm belief that loss prevention starts with the cargo acceptance procedure and the control measures that are possible to detect mis- and un-declared Dangerous Goods. Stowage of containers based on risk evaluation is an effective supporting measure however it cannot address mentioned mis- and un-declaration issues. Countermeasures to assist in firefighting onboard are supportive and increases the chance of keeping a fire exposed vessel manoeuvrable and stability intact however the thousands of cargo combinations that are possible have clearly showed that there is a considerable risk of reaching self-enhancing fire development despite efforts to extinguish both on and under deck. Secondly it is of utmost importance that quality control of accepted shipments is considered and controlled systematically, i.e., that packers are educated according to the CTU code, that correct packaging is used, and container stuffed correctly. A know-your-client approach which, when relevant includes a quality assessment or inspection of the production process, ISO certification control etc., would be very relevant as a harmonized industry initiative. It should also be mentioned that the IMO circular on container inspection is being reviewed and aims to make use of CTU guide principles mandatory. Finally, we strongly advocate and would like to express that a goal-based approach which is in line with IMO practice should be followed, thereby ensuring that desired results are outcome driven and not technology driven. It should be noted that whilst publicly available detailed cargo information is unavailable for the Express Pearl incident, stowage would have benefitted from the Risk-Zone Based Dangerous Goods Stowage Concept, since commodities that are not effectively extinguished with CO2 have been moved to deck stowage and secondly, since the concept also caters for non-block stowage specific to commodities. Whilst radiant heat of such temperatures as can be interpreted from the publicly available media, can travel downwards if the right receptor is available below deck, the Risk-Zone Based Dangerous Goods Stowage Concept segregation and positioning of Dangerous Goods, could possibly have enabled a more effective on deck firefighting and an effective CO2 underdeck extinguishing since oxidizing commodities are not allowed under deck and block stowage is regulated. | The Contain project raises a number of unknowns e.g. time for smoke/fire to escape a container all depended on the characteristic of the container. https://brandogsikring.dk/files/Pdf/FogU/Contain/DBI%20CONTAIN%20Project%20-%20Final%20Report.pdf |  | 1. Solutions need to be flexible and should look into all possible fire scenarios. 2. Increasing number of ships are now fuelled with LNG, which can have devastating effects in case of fires. Therefore, improvement in fire safety systems is a must. 3. Once more advanced technological systems are put in place, there is a need to improve the crew training as well.